## Slide 1
MODBUS ATTACK & DEFEND
The oldest industrial protocol still running the world — four data banks, one byte of intent, and no authentication anywhere.
Modicon 1979 · Modbus Organization spec v1.1b3
Purdue L1–L2 · HMI/SCADA ↔ PLC/RTU · serial gateways
registers are big-endian 16-bit words
Weaponised by FrostyGoop / BUSTLEBERM — Lviv, Jan 2024
Modbus has no users, no passwords and no sessions. Whoever can reach tcp/502 is the master. The only question left is which function code, against which register.
1 WHERE IT LIVES
VARIANTS
Modbus/TCP MBAP header + PDU, port 502
Modbus RTU RS-485/232 serial, CRC-16
Modbus ASCII ':' … CRLF framing, LRC
RTU-over-TCP raw serial ADU in TCP — no MBAP
Modbus Security TLS on 802 — near-absent
PORTS
502/tcp Modbus/TCP ← Shodan port:502
802/tcp Modbus/TCP Security (TLS)
no std port RTU-over-TCP on Moxa /
Lantronix / Digi gateways
Serial-to-Ethernet gateways are the soft edge: they turn a physical-access problem into a routable one. Inventory every one of them.
2 THE FOUR DATA BANKS
BANK BITS ACC FUNCTION CODES
Coils 1 R/W 1 / 5 / 15
physical digital OUTPUTS — relay, valve, motor
Discrete Inputs 1 R 2
physical digital inputs
Input Registers 16 R 4
analog inputs / measured values
Holding Registers 16 R/W 3 / 6 / 16 / 22 / 23
setpoints and parameters
⚠ THE ADDRESSING TRAP
Your documentation says 40001. The wire says 0x0000.
The vendor 4xxxx convention is 1-based and bank-prefixed. The PDU carries a 0-based offset within its bank. Holding register 40001 is wire address 0.
Get this wrong and you hunt the wrong register — or write to one.
32-bit and float values span TWO registers, and the word order is vendor-dependent. Never assume.
3 FRAME ANATOMY
MODBUS/TCP ADU
┌──────────┬──────────┬────────┬──────┬────┬───────┐
│ Trans ID │ Proto ID │ Length │ Unit │ FC │ data │
│ 2 B │ 2 B │ 2 B │ 1 B │1 B │ n B │
└──────────┴──────────┴────────┴──────┴────┴───────┘
MBAP header — 7 bytes, big-endian PDU
Trans ID echoed by the server; a compliant master increments per request.
Static across many requests = replay / injection tell.
Proto ID MUST be 0x0000. Non-zero on 502 = malformed, tunnelled or fuzzing.
Length bytes of Unit ID + PDU. Parse by this — one TCP segment can
carry several back-to-back frames.
Unit ID slave address behind a gateway. UNIT 0 = BROADCAST
A write to unit 0 hits every device on the serial leg, unacknowledged.
FC | 0x80 exception response — MSB set, plus a 1-byte exception code.
RTU-OVER-TCP HAS NO MBAP
Slave Addr (1B) + FC (1B) + data + CRC-16 (2B, poly 0xA001). Your dissector will not find it on its own — Wireshark: Decode As → Modbus RTU. Miss this and a whole gateway's traffic reads as noise.
4 FUNCTION CODES — THE WEAPON RACK colour = what it does to the process
RECON
READ
WRITE
CONTROL / DESTRUCTIVE
VENDOR
READ — the baseline noise of every plant network
01 0x01 Read Coils coils read digital output state
02 0x02 Read Discrete Inputs discrete in read digital input state
03 0x03 Read Holding Registers holding read setpoints — FrostyGoop recon half
04 0x04 Read Input Registers input read measured values
07 0x07 Read Exception Status — serial: 8 exception bits
11 0x0B Get Comm Event Counter — serial diagnostics
12 0x0C Get Comm Event Log — serial diagnostics
20 0x14 Read File Record file config / firmware image staging
24 0x18 Read FIFO Queue — queue contents
RECON — unauthenticated device fingerprinting
17 0x11 Report Server ID — vendor + device enumeration
43 0x2B Encap. Interface Transport MEI 0x0E Read Device ID: vendor, product, rev
WRITE — every one of these moves physical process
05 0x05 Write Single Coil coils FORCE one output ON/OFF — valve, relay, motor
06 0x06 Write Single Register holding one setpoint — FrostyGoop write vector
15 0x0F Write Multiple Coils coils bulk output force
16 0x10 Write Multiple Registers holding bulk setpoint — FrostyGoop write vector
21 0x15 Write File Record file writes the device config store
22 0x16 Mask Write Register holding AND/OR read-modify-write of one register
23 0x17 Read/Write Multiple Regs holding read + write in ONE PDU
CONTROL — see panel 5 for the sub-function detail
08 0x08 Diagnostics — restart · force listen-only · clear counters
VENDOR / RESERVED
65-72 Vendor-defined range — legal but proprietary — baseline, do not assume
100-110 Vendor-defined range — anything outside these = protocol violation
5 FC 8 DIAGNOSTICS & EXCEPTIONS
FC 8 SUB-FUNCTIONS
0x00 Return Query Data loopback echo
0x01 Restart Communications Option DEVICE RESTART — T0816
0x02 Return Diagnostic Register read diag register
0x03 Change ASCII Input Delimiter framing change
0x04 Force Listen Only Mode SILENCES THE SLAVE — DoS, T0814
0x0A Clear Counters and Diag Register ANTI-FORENSICS
0x0B Return Bus Message Count counter read
0x0C Return Bus Comm Error Count counter read
0x0D Return Bus Exception Error Count counter read
0x0E Return Slave Message Count counter read
0x0F Return Slave No Response Count counter read
0x10 Return Slave NAK Count counter read
0x11 Return Slave Busy Count counter read
0x12 Return Bus Char Overrun Count counter read
0x14 Clear Overrun Counter and Flag counter clear
EXCEPTION CODES response = FC | 0x80, then one byte
0x01 Illegal Function
0x02 Illegal Data Address
0x03 Illegal Data Value
0x04 Server Device Failure
0x05 Acknowledge
0x06 Server Device Busy
0x08 Memory Parity Error
0x0A Gateway Path Unavailable
0x0B Gateway Target Failed To Respond
EXCEPTIONS ARE THE LOUDEST RECON SIGNAL
Bursts of 0x01 / 0x02 across many addresses and function codes = enumeration, fuzzing or exploit probing. They ride in the RESPONSE, so you catch them even when you missed the request.
6 ATTACKER PLAYBOOK ICS Kill Chain — Stage 2
1 DISCOVER
Scan tcp/502 — Shodan port:502 still returns internet-facing PLCs daily. Behind a gateway, sweep Unit IDs 1–247 to find what is on the serial leg.
2 FINGERPRINT
FC 43 / MEI 0x0E Read Device Identification returns vendor, product code and revision. FC 17 Report Server ID does the same on serial. No session, no credentials, no trace beyond a log line.
3 MAP THE PROCESS
Walk register and coil ranges with FC 1/2/3/4. Exception 0x02 Illegal Data Address tells you exactly where the map ends. Reads are indistinguishable from the HMI's own polling — this recon is free.
4 MANIPULATE
FC 5/15 force coils, which are physical outputs. FC 6/16/22/23 write registers, which are setpoints. FC 23 reads and writes in a single PDU.
5 DISRUPT
FC 8 sub 0x04 Force Listen-Only silences a slave outright. Sub 0x01 restarts it. A broadcast write to Unit 0 hits an entire serial leg at once, unacknowledged.
6 COVER TRACKS
FC 8 sub 0x0A Clear Counters and Diagnostic Register wipes the device's own record of the errors you just caused.
WHY IT WORKS
No authentication, no encryption, no integrity, no session. Anyone on the segment is the master. FrostyGoop needed exactly three function codes — 3, 6 and 16 — and a stock Go Modbus library.
7 DEFENDER PLAYBOOK capture → parse → triage
CAPTURE
bpf: tcp port 502 trunk: (tcp port 502) or (vlan and tcp port 502)
Tap the cell/process switch. A 50-PLC 1 Hz poll loop is only ~1–5 MB/min — keep full payload.
ZEEK
modbus.log · ICSNPP: modbus_detailed.log · modbus_read_write.log
ICSNPP gives you unit_id, address, quantity and the DECODED VALUE written.
SURICATA — native modbus keyword
modbus: function [5,6,15,16]; modbus: function 8, subfunction 1;
modbus: unit 0;
WIRESHARK
modbus.func_code == 8 && modbus.diagnostic.sub_function == 4
modbus.mei == 0x0e mbtcp.unit_id == 0
TRIAGE — FIVE QUESTIONS, IN ORDER
1 Is it a write or control op? (5/6/15/16/21/22/23 · FC8 restart/listen-only/clear · unit 0)
2 Is the source a baselined master or EWS? 3 Inside a change window?
4 Does the target register match baseline? 5 Read-then-write? Write burst?
Non-baseline source on a write → ESCALATE. Notify ops BEFORE touching the process.
★ THE HIGHEST-VALUE QUERY IN OT
Modbus write function codes from a source that is not in the SCADA-master baseline.
That one query is what would have caught FrostyGoop. It needs no threat intel, no signature and no vendor feed — only an accurate list of who is allowed to write. Everything else on this poster is refinement.
8 NORMAL vs SUSPICIOUS
NORMAL
· a small, stable set of master IPs
· fixed servers and Unit IDs, regular cadence
· overwhelmingly reads — FC 1/2/3/4
· narrow, consistent register window
· transaction IDs increment; 1:1 request/response
SUSPICIOUS
· write FC from a non-baselined source ← the finding
· coil force 5/15 — physical output manipulation
· write to Unit ID 0 (broadcast)
· read-then-write the same register
· FC8 restart / listen-only / clear counters
· new write target, first-seen master, off-hours
· FC17 / FC43 enumeration from a non-primary source
· non-zero protocol ID, static transaction ID
· unanswered requests (DoS) · phantom responses (spoof)
· Modbus on a non-standard port, or on a public IP
9 HARDENING
1. Modbus has no auth — the network IS the access control. Allowlist master→server pairs.
2. Never expose 502 to the internet. Check Shodan/Censys against your own ASN.
3. Segment cell/area zones; deny 502 across boundaries except named pairs.
4. Filter on function code where the firewall or OT-IDS supports it — deny writes from non-masters.
5. Block Unit ID 0 broadcast writes at the gateway.
6. Alarm on FC8 sub 0x01 / 0x04 / 0x0A — no legitimate poller sends these.
7. Baseline the register and coil map per (server, unit); alert on a new write target.
8. Where the gear supports it, move to Modbus/TCP Security (TLS on 802).
9. Inventory serial-to-Ethernet gateways — they are the quietest way in.
Top 20 Secure PLC Coding Practices · IEC 62443-3-3 · NIST SP 800-82r3
10 ATT&CK for ICS
T0846 Remote System Discovery scanning tcp/502
T0888 Remote System Info Discovery FC17 · FC43 MEI 0x0E
T0855 Unauthorized Command Message any non-authorised write
T0831 Manipulation of Control coil force FC 5/15
T0836 Modify Parameter register write 6/16/22/23
T0806 Brute Force I/O write bursts, range sweeps
T0816 Device Restart / Shutdown FC8 sub 0x01
T0814 Denial of Service FC8 sub 0x04 · flooding
T0856 Spoof Reporting Message injected responses
T0813 Denial of Control the FrostyGoop outcome
T0826 Loss of Availability 600+ buildings, 2 days
SEEN IN THE WILD
FrostyGoop / BUSTLEBERM — Lvivteploenergo, 22–23 Jan 2024. FC 3/6/16 against ENCO controllers.
Function, diagnostic and exception codes verified against the Wireshark Modbus dissector (packet-mbtcp.c/.h) and the Modbus Organization Application Protocol Specification v1.1b3.
Lab reference only — exercise against equipment you are authorised to test. A coil write is a physical output. No client data.
MODBUS — ATTACK & DEFEND
v1.0 · August 2026 · print at 18 × 24 in