## Slide 1
DNP3 ATTACK & DEFEND
The SCADA protocol under the North American grid — three sublayers, one control code, and no idea who you are.
IEEE 1815-2012 · DNP Users Group object library
Purdue L1–L2 · master ↔ outstation (RTU/IED) · long-haul WAN
16-bit link addresses, little-endian · CRC poly 0x3D65
Broken open by Project Robus — Crain & Sistrunk, 2013–14
DNP3 asks twice before it trips a breaker. Select arms the point, Operate fires it — and neither message asks who you are. FC 5 Direct Operate skips the first.
1 WHERE IT LIVES
STACK
DNP3/TCP 20000 — the master usually opens the socket
DNP3/UDP 20000 — rare, and broadcast-capable
DNP3 serial RS-232/485 — same three sublayers, no IP
Serial-over-TCP terminal server — no standard port
DNP3-SAv5 IEEE 1815-2012 auth — no confidentiality
PORTS
20000/tcp DNP3 ← Shodan port:20000
20000/udp DNP3 over UDP, broadcast
19999/tcp dnp-sec / DNP3 over TLS — near-absent
no std port serial tunnel, cellular router, gateway
Master ↔ outstation. Control centre and SCADA front-end processor talking to RTUs, IEDs, protection relays, reclosers, pump stations.
THE LONG-HAUL LINK IS THE SOFT EDGE
Leased line, licensed radio, cellular, microwave. DNP3 legitimately crosses infrastructure you do not own, to sites nobody visits for months. Every one of those paths is an injection point that never touches your fence.
2 THE OBJECT LIBRARY
GROUP VAR OBJECT ACC WHAT IT IS
1 / 2 1-3 Binary Input / Event R breaker OPEN|CLOSED, alarms
10 / 11 1,2 Binary Output Status / Ev R output point as it stands
12 1 Control Relay Output Blk W THE BREAKER — the CROB
20 / 22 1-8 Counter / Event R metering, accumulators
30 / 32 1-8 Analog Input / Event R MW, kV, pressure, level
40 1-4 Analog Output Status R the setpoint as it stands
41 1-4 Analog Output Block W SETPOINT WRITE
50 1,3,4 Time and Date W time sync — and time skew
60 1-4 Class 0 / 1 / 2 / 3 data R the polling shorthand
70 2-7 File transfer RW config + firmware movement
80 1 Internal Indications RW the IIN, as a written object
120 1-9 Secure Authentication v5 — challenge / response
Every request is <FC> on <GROUP>.<VARIATION> over a <QUALIFIER>:<RANGE>.
⚠ THE POINT INDEX IS NOT AN ADDRESS
Group 12 index 7 is Feeder 4 only because the device profile says so. Indices are 0-based, per-group and vendor-assigned — two outstations from two vendors do not share a map, and the standard does not define one.
A capture alone tells you a breaker moved. It never tells you which breaker.
Pull the point list with the PCAP or the evidence is half-blind.
3 FRAME ANATOMY
DNP3 LINK FRAME — three sublayers in every packet
┌───────┬──────┬──────┬──────────┬──────────┬───────┐
│ 05 64 │ LEN │ CTRL │ DEST │ SRC │ CRC │
│ 2 B │ 1 B │ 1 B │ 2 B LE │ 2 B LE │ 2 B │
└───────┴──────┴──────┴──────────┴──────────┴───────┘
user data → 16-byte blocks, each + 2 B CRC poly 0x3D65
── TRANSPORT ── 1 B ── FIR │ FIN │ SEQ 6 bits
── APPLICATION ── AC 1 B │ FC 1 B │ objects … + IIN 2 B on 129/130
05 64 starts every frame. Off-port, a chance 0x0564 that fails CRC is not DNP3.
LEN counts CTRL → end of user data, excludes the CRCs. Max 255.
CTRL carries DIR, PRM, FCB/FCV and the data-link function code.
DEST / SRC are DNP3 link addresses — not the IP. 0xFFFD–0xFFFF broadcast
CRC per 16-byte block — a mismatch on 20000 is evidence, not noise.
THE LINK ADDRESS IS A SECOND IDENTITY
Your firewall sees 10.30.4.12. The protocol sees outstation 47. Nothing in the frame binds them together.
Alert on the PAIR: a known master IP with an unexpected source link address, or a known link address arriving from a new IP.
4 FUNCTION CODES — THE WEAPON RACK colour = what it does to the physical process
RECON
READ
WRITE
CONTROL / DESTRUCTIVE
AUTH
READ — 99% of a healthy DNP3 network is these four
01 0x01 Read Class & integrity polls · recon when the source is new
129 0x81 Response the outstation reply — carries the IIN
130 0x82 Unsolicited Response event push with no poll — enabled per point
00 0x00 Confirm link and application acknowledgement
23 0x17 Delay Measurement link timing 24 0x18 Record Current Time
CONTROL — Select-Before-Operate, and the way round it
03 0x03 Select arms a point — control intent, nothing moves T0855
04 0x04 Operate fires the armed point — a physical change T0831
05 0x05 Direct Operate NO Select. one message, identical result T0831
06 0x06 Direct Operate No Ack same again, and no response to correlate on T0831
WRITE — state change without a control code
02 0x02 Write outputs, TIME, configuration values T0836
07 – 12 Freeze / Freeze & Clear ± time, ± no-ack — wipes accumulators T0836
22 0x16 Assign Class changes what gets reported, and when T0856
20 0x14 Enable Unsolicited flood or mask the event stream
21 0x15 Disable Unsolicited SILENCES the outstation — denial of view T0815
DESTRUCTIVE — loss of control on one device, or on all of them
13 0x0D Cold Restart full outstation reboot T0816
14 0x0E Warm Restart application restart T0816
18 0x12 Stop Application halts the outstation application T0816
15 0x0F Initialize Data data points back to defaults T0836
16 / 17 Init / Start Applicationreinitialise, then run T0855
19 0x13 Save Configuration persist the running config to NVRAM T0836
31 0x1F Activate Configuration commit a staged configuration T0836
FILE — approximately never in normal telemetry
25 – 30 Open/Close/Delete/Info + Authenticate, Abort File — config & firmware T0845
AUTH — DNP3 Secure Authentication v5, where it is switched on
32 0x20 Authenticate Request SAv5 is on the wire — not that it covers this FC
33 0x21 Authenticate Error challenge failed, or the key is wrong
5 THE CROB & THE IIN
GROUP 12 VAR 1 — CONTROL RELAY OUTPUT BLOCK
┌────────────┬───────┬──────────┬──────────┬────────┐
│ CTRL CODE │ COUNT │ ON TIME │ OFF TIME │ STATUS │
│ 1 B │ 1 B │ 4 B │ 4 B │ 1 B │
└────────────┴───────┴──────────┴──────────┴────────┘
CONTROL CODE bit 7 6 │ 5 │ 4 │ 3 2 1 0
[TCC]│ C │ Q │ [OP TYPE]
TCC 0 NUL 1 CLOSE 2 TRIP
OP 0 NUL 1 PULSE_ON 2 PULSE_OFF 3 LATCH_ON 4 LATCH_OFF
0x41 = CLOSE + PULSE_ON 0x81 = TRIP + PULSE_ON
Eleven bytes. One of them is intent.
IIN — INTERNAL INDICATIONS 2 B on every FC 129 / 130
FIRST OCTET SECOND OCTET
0x01 Broadcast msg received 0x01 Function code not supported
0x02 Class 1 events available 0x02 Object unknown
0x04 Class 2 events available 0x04 Parameter error
0x08 Class 3 events available 0x08 Event buffer overflow
0x10 Need time — sync request 0x10 Operation already executing
0x20 Local control — LOCAL 0x20 Configuration corrupt
0x40 Device trouble 0x40 reserved
0x80 Device restart 0x80 reserved
QUALIFIER — how a request addresses the points
0x00 / 0x01 8- / 16-bit start-stop range 0x06 all points, no range
0x07 / 0x08 limited quantity, 8/16-bit 0x17 / 0x28 index prefix + count
A Class 0 integrity poll is 01 3C 01 06. A single-point CROB is 0C 01 17 01.
★ THE IIN IS A FREE INTRUSION DETECTOR
Device Restart, Device Trouble and Configuration Corrupt confirm that something changed state — they are the outstation reporting its own outage.
A burst of Function-code-not-supported / Object-unknown / Parameter-error is somebody enumerating or fuzzing that outstation.
It rides in the RESPONSE, so you catch it even when you missed the request — and nobody reads it.
6 ATTACKER PLAYBOOK ICS Kill Chain — Stage 2
1 DISCOVER
Scan tcp/20000 — Shodan port:20000 still returns internet-facing outstations. Behind a serial gateway, sweep DNP3 destination link addresses 0–65519 to map every device on the loop from one IP.
2 FINGERPRINT
FC 1 Read of Group 60 Var 1 — a Class 0 integrity poll — returns the entire static point map: every binary input, analog, counter and output the outstation owns. No session, no credential. It is byte-identical to the master's own poll, so the recon is free.
3 MAP THE PROCESS
Walk Group 30/40 for values and Group 12/41 for controls. IIN Object-unknown and Parameter-error tell you exactly where the map ends. Group 80 hands you the outstation's own indications.
4 ARM
FC 3 Select against a control point — and stop. A confirmed Select proves the point is real and armable and moves nothing physical. Select-without-Operate is control-point enumeration, and it is invisible to anything watching only for Operate.
5 MANIPULATE
FC 4 Operate fires the armed point; FC 5/6 Direct Operate skips the Select entirely. CROB control code 0x81 trips, 0x41 closes. FC 2 Write moves analog setpoints and the clock. Aim any of it at link address 0xFFFD–0xFFFF and it lands on every outstation at once.
6 BLIND & COVER
FC 21 Disable Unsolicited stops event reporting and the master keeps its last picture. FC 9/10 Freeze-and-Clear wipes the accumulators. FC 13/14 restart the device, FC 18 stops the application, FC 25–30 move files off it.
WHY IT WORKS
No authentication, no encryption, no message integrity in the base protocol. Select-Before-Operate is an interlock against a mis-click, not an authorisation step — and Direct Operate is in the same specification. SAv5 exists, is optional, and is frequently scoped to a subset of function codes on a subset of devices.
7 DEFENDER PLAYBOOK capture → parse → triage
CAPTURE
bpf: tcp port 20000 trunk: (port 20000) or (vlan and port 20000)
Tap the control-LAN / RTU switch. A 20-outstation substation with integrity polls and Class 1 events runs ~10–50 MB/min. Include udp/20000 and the serial-gateway port.
ZEEK — ICSNPP-DNP3
dnp3.log · dnp3_control.log · dnp3_objects.log
fc_request, fc_reply, iin, dnp3_src, dnp3_dst — the control log decodes the CROB to trip/close with on/off time; the objects log gives group, variation, qualifier and range.
SURICATA / SNORT 3 — native dnp3 inspector
dnp3_func:operate; dnp3_func:direct_operate; dnp3_func:cold_restart;
dnp3_ind:device_restart; dnp3_obj:12,1; dnp3_data; ← CRC-stripped
WIRESHARK
dnp3.al.func in {3 4 5 6} dnp3.al.func in {13 14 18 21}
dnp3.al.iin.dr dnp3.src / dnp3.dst dnp3.al.obj == 0x0c01
TRIAGE — FIVE QUESTIONS, IN ORDER
1 Is it a control, restart or config op? (2/3/4/5/6 · 13/14/18 · 15/16/19/31 · 21 · 25–30)
2 From the authorised master? Check the source IP and the source link address, as a pair.
3 Inside a change window, against a work order? 4 Did an Operate follow a Select to the same point?
5 Broadcast address, or IIN Device Restart / Config Corrupt? → confirmed. Non-master control or bypassed SBO → ESCALATE.
★ THE HIGHEST-VALUE QUERY IN OT
Every DNP3 function code on the network that is not 1, 129 or 130.
Read, Response and Unsolicited Response are almost all of a healthy network — telemetry is polling, and polling is boring. Everything left over is the entire control plane, and on most utilities a month of it is short enough to read by eye and put a work order against every line.
If the list is too long to read, that is the finding — and detection is not the first job. Working out why your control plane is that noisy is.
8 NORMAL vs SUSPICIOUS
NORMAL
· one master, or a few redundant ones, to a fixed outstation set
· FC 1 Read + FC 129 Response at a steady poll cadence
· FC 130 Unsolicited only where it was explicitly enabled
· periodic FC 23 / 24 time sync from the master
· stable IP ↔ DNP3 link-address bindings, per device
· control (3 → 4) rare, in hours, operator-initiated, from the master
· IIN quiet — class-event bits and need-time, nothing else
SUSPICIOUS
· control FC from a non-master IP or link address — the finding
· Operate with no preceding Select — SBO bypass, or a capture gap
· Select with no Operate — control-point enumeration
· Direct Operate 5 / 6 where the standard says Select-Before-Operate
· broadcast control to link address 0xFFFD–0xFFFF
· Disable Unsolicited, Cold/Warm Restart or Stop Application off-hours
· file operations 25–30 against a telemetry outstation
· IIN Device Restart or Configuration Corrupt appearing unbidden
· bursts of Object Unknown / Parameter Error / FC-not-supported
· one source touching many DNP3 destination link addresses
· DNP3 on a public IP, or on a non-standard port
· CRC mismatch on port 20000
9 HARDENING
1. Allowlist master → outstation pairs on both IP and DNP3 link address. The network IS the access control.
2. Never expose 20000 to the internet. Check Shodan and Censys against your own ASN.
3. Enable DNP3-SAv5 where the devices support it — and record which function codes it actually covers.
4. Disable Direct Operate at the outstation wherever the engineering standard says Select-Before-Operate.
5. Assign link addresses uniquely, and suppress response to broadcast where the device allows it.
6. Alarm on FC 13 / 14 / 18 / 21 and on any file operation, unconditionally.
7. Log the IIN. Device Restart and Configuration Corrupt should page a human.
8. Terminate serial tunnels at a known gateway. Inventory every terminal server and cellular router.
9. Keep the point list with the capture — evidence without the device profile is half-blind.
IEC 62443-3-3 · NIST SP 800-82r3 · NERC CIP-005 / 007 · IEEE 1815-2012 SAv5
10 ATT&CK for ICS
T0846 Remote System Discovery scanning tcp/20000
T0888 Remote System Info Discovery Class 0 integrity poll
T0840 Network Connection Enum link-address sweep
T0885 Commonly Used Port 20000/tcp, 20000/udp
T0855 Unauthorized Command Message Select / Operate from non-master
T0831 Manipulation of Control CROB Operate on a breaker
T0836 Modify Parameter Write, AO block, Save/Activate Config
T0806 Brute Force I/O Select/Operate sweep across indices
T0816 Device Restart / Shutdown FC 13 / 14, Stop Application 18
T0815 Denial of View Disable Unsolicited 21
T0814 Denial of Service poll starvation, restart bursts
T0856 Spoof Reporting Message injected Unsolicited Responses
T0845 Program Upload file operations 25–30
T0800 Activate Firmware Update Modefile ops staging firmware
SEEN IN THE WILD
Project Robus — Crain & Sistrunk, 2013–14. Dozens of DNP3 stack flaws disclosed through ICS-CERT; a malformed frame from an outstation could crash the master. The trust runs both ways.
Function codes, object groups, IIN bits and detection syntax verified against IEEE 1815-2012, the DNP Users Group object library, the Wireshark DNP3 dissector (packet-dnp3.c) and CISA/INL ICSNPP-DNP3.
Lab reference only — exercise against equipment you are authorised to test. An Operate is a breaker, not a finding. No client data.
DNP3 — ATTACK & DEFEND
v1.0 · September 2026 · print at 18 × 24 in