## Slide 1
CIP / EtherNet/IP ATTACK & DEFEND
The Common Industrial Protocol on the wire — service codes, object classes, and how both sides read them.
ODVA · CIP Networks Library Vol 1
Purdue L1–L2 · Rockwell ControlLogix / CompactLogix /
Micro8xx / PowerFlex · little-endian on the wire
Spoken by PIPEDREAM (CODECALL) · BAUXITE (AA26-097A)
CIP is objects. Every request — benign or hostile — is one sentence: <SERVICE> on <CLASS> : <INSTANCE> : <ATTRIBUTE>. Learn the triple and the protocol has no secrets.
1 WHERE IT LIVES
CIP objects · services · EPATH ← application layer
─────────────────────────────────────────────
EtherNet/IP (Vol 2) DeviceNet (Vol 3)
ControlNet (Vol 4) CompoNet (Vol 6)
CIP Safety (Vol 5) CIP Security (Vol 8)
─────────────────────────────────────────────
TCP / UDP / IP → Ethernet
PORTS
44818/tcp explicit messaging (req/resp)
44818/udp ListIdentity discovery ← Shodan signature
2222/udp implicit class-1 cyclic I/O
2221/both CIP Security TLS/DTLS — rarely on
Explicit = request/response, on demand. Implicit = cyclic I/O, no per-packet handshake, trivially spoofable.
2 THE OBJECT MODEL
DEVICE
└─ CLASS 0x01 Identity
└─ INSTANCE 1, 2, 3 …
└─ ATTRIBUTE 7 = firmware rev
SERVICE 0x0E Get_Attribute_Single
acts on that path, encoded as EPATH segments.
READS AS
0x0E 0x01 : 1 : 7 → read firmware rev
⚠ TRAP — SERVICE CODES ARE CLASS-SCOPED
0x4E = Forward_Close on class 0x06, Read Holding Regs on 0x44, Read-Modify-Write on Logix tags. Never alert on a service without its class.
3 SESSION & CONNECTION CHAIN
1 ListIdentity 0x0063 who is out there, what firmware
2 ListServices 0x0004 what encapsulation is offered
3 RegisterSession 0x0065 → session handle
NO CREDENTIALS. The handle is a cookie, not a login.
4a SendRRData 0x006F unconnected explicit (UCMM)
4b Forward_Open 0x54 class 0x06 → Connection ID pair
SendUnitData 0x0070 connected explicit / class-3
5 class-1 implicit I/O udp/2222 cyclic
6 UnRegisterSession 0x0066
WHY THIS IS THE WHOLE FIGHT
Steps 1–3 are unauthenticated and pre-session. An attacker learns vendor, product code, serial and firmware revision — enough to pick a CVE — before sending a single command.
4 SERVICE CODES — THE WEAPON RACK colour = what it does to the process
RECON
READ
WRITE
CONTROL / DESTRUCTIVE
PIVOT
UNIVERSAL — valid on almost any object class
0x01 Get_Attributes_All any dump every attribute of an instance
0x0E Get_Attribute_Single any read one attribute
0x11 Find_Next_Object_Instance any walk instances — enumeration primitive
0x03 Get_Attribute_List any batch read
0x04 Set_Attribute_List any batch write of attributes
0x10 Set_Attribute_Single any change one config value
0x02 Set_Attributes_All any overwrite the whole instance
0x08 Create any instantiate an object
0x09 Delete any destroy an instance
0x0A Multiple_Service_Packet any batch N services in one request — evasion
0x16 Save any persist config to non-volatile store
0x15 Restore any roll config back from store
0x05 Reset Identity 0x01 type 0 = restart · type 1 = FACTORY DEFAULT
0x06 Start Identity 0x01 mode change → RUN
0x07 Stop Identity 0x01 mode change → PROGRAM · process halt
CONNECTION MANAGER — class 0x06
0x54 Forward_Open 0x06 open a CIP connection — precursor to control
0x5B Large_Forward_Open 0x06 same, >511-byte payloads
0x4E Forward_Close 0x06 tear the connection down
0x52 Unconnected_Send 0x06 route a request through a bridge / backplane
LOGIX TAG SERVICES — Symbol class 0x6B
0x4C Read Tag 0x6B read a tag by symbolic name
0x52 Read Tag Fragmented 0x6B large read
0x4D Write Tag 0x6B write a setpoint / data-table value
0x53 Write Tag Fragmented 0x6B large write
0x4E Read-Modify-Write 0x6B atomic bit set — flip a single coil
LEGACY TUNNEL — PCCC class 0x67
0x4B Execute_PCCC 0x67 tunnel SLC-500 / PLC-5 commands behind CIP
5 HIGH-VALUE OBJECT CLASSES
0x01 Identity vendor · serial · FIRMWARE REV → CVE. Hosts Reset.
0x02 Message Router dispatches every explicit request
0x04 Assembly the I/O data blob. Write = direct process manipulation.
0x06 Connection Manager Forward_Open, Unconnected_Send (routing / pivot)
0x0F Parameter device configuration values
0x37 File EDS + FIRMWARE download chain
0x41 Event Log device-side evidence — DEFENDERS: pull this
0x44 Modbus Modbus-over-CIP bridge — protocol hop
0x47 DLR ring topology control — disrupt = network partition
0x5D CIP Security the control plane, if it is switched on
0x5E EtherNet/IP Security TLS/DTLS config
0x5F Certificate Mgmt device certificates
0x67 PCCC legacy SLC / PLC-5 tunnel
0x6B Symbol (Logix) the TAG NAMESPACE. Enumerate = read the process design.
0x6C Template (Logix) UDT structure definitions
0xF3 Conn. Config (CCO) connection provisioning
0xF4 Port backplane / network port map — reveals topology
0xF5 TCP/IP Interface write = re-IP the device
0xF6 Ethernet Link link config + counters
THE CROWN JEWEL
Symbol object 0x6B + Get_Instance_Attribute_List dumps every tag name in the controller. PUMP_1_SPEED, VALVE_HS201_CMD — the process design, unauthenticated.
6 ATTACKER PLAYBOOK ICS Kill Chain — Stage 2
1 DISCOVER
ListIdentity 0x0063 broadcast on udp/44818, or a unicast sweep. Shodan: port:44818. Returns vendor, product code, serial, firmware rev, IP — unauthenticated, pre-session.
2 ENUMERATE
Get_Attributes_All on Identity · Find_Next_Object_Instance to walk classes · Get_Instance_Attribute_List on Symbol 0x6B to dump the tag namespace. Tag names leak the process semantics.
3 ESTABLISH
RegisterSession 0x0065 — no credentials required. Forward_Open 0x54 for a class-3 connection when you need ordered, connected messaging.
4 MANIPULATE
Write Tag 0x4D to a setpoint · Set_Attribute_Single 0x10 to change config · write the Assembly object 0x04 for direct I/O. Batch with Multiple_Service_Packet 0x0A to compress the burst.
5 DISRUPT
Stop 0x07 drops the controller to PROGRAM · Reset 0x05 type 1 restores factory defaults · flood Forward_Open to exhaust the connection table.
6 PERSIST / DESTROY
Firmware push via the File object 0x37 · PCCC tunnel 0x4B to legacy SLC/PLC-5 behind the controller · Unconnected_Send 0x52 to route deeper into the backplane.
WHY IT WORKS
Base CIP has no authentication, no encryption and no message integrity. The session handle is not a credential. Off-the-shelf tooling speaks it fluently: pycomm3, cpppo, plcscan, Metasploit ethernetip modules.
7 DEFENDER PLAYBOOK capture → parse → triage
CAPTURE
bpf: tcp port 44818 or udp port 2222 or udp port 44818 or port 2221
TAP in preference to SPAN, positioned at the L2/L3 conduit.
ZEEK — ICSNPP-ENIP
enip.log · cip.log · cip_io.log · cip_identity.log
→ service, class, instance, tag, status per request
SURICATA
enip_command:0x006f; cip_service:0x4d; cip_class:0x6b
Always pair the service with the class — see TRAP, panel 2.
WIRESHARK
cip.service == 0x4d && cip.class == 0x6b
enip.command == 0x63
TRIAGE LOGIC
Is the service Write / Set / Stop / Reset / Forward_Open-then-write?
→ is the source an authorised EWS or HMI in the baseline?
→ inside a change window, matching a ticket?
write-class + non-EWS + no window → ESCALATE
★ THE FALSE-ZERO RULE
A manipulation-class count of 0 is a defensible Negative only when the benign-runtime classes — Read Tag 0x4C, Write Tag 0x4D, Forward_Open 0x54 — are non-zero in the same capture. Those prove the capture point actually sees the CIP conversation.
All-zero across every service is a capture gap, not a clean hunt. Report Non-Conclusive, never Negative.
8 NORMAL vs SUSPICIOUS
NORMAL
· HMI/SCADA polling Read Tag at a steady cadence
· EWS writes during a known change window
· class-1 I/O between established producer/consumer pairs
· ListIdentity from the asset-inventory scanner
SUSPICIOUS
· Write Tag / Set_Attribute / Stop / Reset from a non-EWS source
· ListIdentity from an internet-side or first-seen internal IP
· first-seen class-1 producer to a controller
· Forward_Open followed by a burst of writes
· Execute_PCCC from an unexpected host
· Multiple_Service_Packet batching write services
· Symbol-object enumeration sweep
9 HARDENING
1. Controller keyswitch in RUN — a hardware veto on remote mode change and download.
2. Enable CIP Security (Vol 8): TLS/DTLS on 2221, device authentication and integrity.
3. Segment into cell/area zones; conduit-filter 44818 and 2222 to named EWS/HMI only.
4. Allowlist by source — CIP has no auth, so the network IS the access control.
5. Disable unused objects; strip the PCCC object where no legacy gear sits behind it.
6. Signed firmware only; monitor the File object 0x37.
7. Baseline the CIP conversation: which source, which service, which class.
8. Ship the device Event Log (0x41) to the SIEM.
9. Never expose 44818 to the internet — check Shodan/Censys against your own ASN.
Top 20 Secure PLC Coding Practices · IEC 62443-3-3 · NIST SP 800-82r3
10 ATT&CK for ICS
T0846 Remote System Discovery ListIdentity sweep
T0888 Remote System Info Discovery Get_Attributes_All
T0861 Point & Tag Identification Symbol 0x6B enumeration
T0855 Unauthorized Command Message any unsanctioned service
T0836 Modify Parameter Write Tag / Set_Attribute
T0843 Program Download logic transfer to controller
T0845 Program Upload logic theft
T0889 Modify Program logic tamper
T0858 Change Operating Mode Start 0x06 / Stop 0x07
T0816 Device Restart / Shutdown Reset 0x05
T0800 Activate Firmware Update Mode File object 0x37
SEEN IN THE WILD
PIPEDREAM / CODECALL (CHERNOVITE) · BAUXITE Rockwell campaign, CISA AA26-097A
Hex values verified against the Wireshark ENIP/CIP dissectors (packet-enip.c, packet-cip.h/.c), ODVA EtherNet/IP Developers Guide, and Rockwell Logix 5000 Data Access (1756-PM020).
Lab reference only — exercise against equipment you are authorised to test. CIP writes move physical process. No client data.
CIP / EtherNet/IP — ATTACK & DEFEND
v1.0 · August 2026 · print at 18 × 24 in